## Slide 1: Smart Grids for the German „Energiewende“
Prof. Dr.-Ing. Markus Zdrallek Wuppertal University
22nd of October 2019
Hanoi, Vietnam

## Slide 2: Main political framework
EU: Clean Energy for all Europeans Package (till 2030)
  Reducing CO2-emissions by 40 %
  Increasing energy efficiency by 32,5 %
  Covering 30 % of the energy demand by renewable sources
Germany: Energy Concept 2050 of the German Government
  Covering 80 % of the electrical energy demand by renewable sources
Challenge for grids:
Connecting enormous numbers of renewable power plants to the grid while keeping the high quality-of-supply level with less cost for grid enhancement.

## Slide 3: What happens to the German grid ?
Wind Power
Photovoltaics
No Nuclear Power
Change in Generation
Comb. Heat/Power plants
Biomass
New electrical loads
E-mobility
Air condition
Heat pumps
Storage units

## Slide 4: German „Energiewende“ – Development of the installed renewable energy
…
6,6
2030
197,5
Prognosis
Source: Based on renewable energy statistics working group (AGEE-Stat)
Peak load Germany: 82 GW !
Notes: The figure visualizes the development of the installed capacity of renewable energies. In 2018, the installed capacity was 118.3 GW. As can be seen, the annual increase in capacity in recent years has fluctuated around the value of 6.6. There are various ramp-up scenarios for the further development of renewable energies. If we simply assume that the trend shown will continue over the next few years, we would end up with almost 200 GW by 2030.

## Slide 5: Challenges for the distribution grids
Strongly increasing distributed generation especially in rural Medium- and Low-Voltage-grids leads to:
  Power flow inversion: (Rural) grids are rather collection than distribution grids (“green grids”)
  Local violations of the permitted voltage rage
  Component overloads
Voltage
Length of the line
Ur + 10%
Ur - 10%
72,1 A
129,8 A
187,6 A
Cable overload!
NAYY 4x50 SE, Ir = 142 A
10 kV / 0,4 kV
St,r = 100 kVA
Solution 2:
Intelligent control (Smart Grids)
Solution 1:
Expensive enhancement of grid capacity

## Slide 6: Enhancement of Grid Capacity (Solution 1)
Concrete Measures:
Increase capacity of Medium Voltage Grid as foreseenin scenario 2030
Adherence to today’s guidelines in 2030
30 Mio. € investments until 2030 in MV
Massive additional investments in LV- and HV-grids
  New 55 km cables (300 mm²)
  New 9 MV satellite grids (81 km, 800 mm²)
  New 2 HV/MV-substations

## Slide 7: Smart Low-Voltage Grid Concept
smart RTU
– automation intelligence–
self-sustaining monitoring and control of low voltage grids
substation
broadband powerline communication
Low Voltage Grid State Identification
determination of desired values for decentralized generation units and consumer loads
output:
voltage control
power factor control
active power control
technical data
topology
data conditioning
decentralized sensor/actuator
decentralized sensor
electric powered vehicles, decentralized power generation units, heat pumps, accumulators
system operation
grid monitoring
grid control

## Slide 8: Smart Low-Voltage Grids (Solution 2)
Satellite-View
Grid-View
11kWp up to 26kWp

## Slide 9: Smart LV-Grids (Solution 2)
Hardware:
Broadband powerline communication infrastructure
6 decentralized direct measurement units
3 SmartRTU in 3 MV/LV-substations with
8 points of current measurement

## Slide 10: Smart Medium-Voltage Grids
Transferring the Concept to Medium-Voltage level
Ensures cost-efficient integration of distributed generation on all distribution levels

## Slide 11: Smart Meter Rollout in Germany
Pilot phase
SM-Sys
Optional Installation SM-Sys
Consumption < 6.000 kWh/a (§29 (2), Nr. 1)
Mandatory
Installation SM-Sys
Generating plants: Nominal power > 7 kW (§29 (1), no. 2)
Generating plants: Nominal power 1-7 kW (§29 (2), no. 2)
Consumption 6.000 – 10.000 kWh/a (§29 (1), 1)
Consumption 10.000 – 20.000 kWh/a
Consumption > 20.000 kWh/a (§21 (1), no. 3)
Mandatory Installation Digital Meter
Smart Meter, assuming no SM-Sys installed and economically justifiable (§29 (3))
Rollout process: mandatory installation for digital meters and smart meter systems. Source: Own representation based on the metering point operating act.
2014
2015
2017
2016
2018
2019
2021
2022
2020
2023
2024
2026
2025
2028
2027
2030
2029
2032
2031
Notes: The legal basis for placing smart meters on the market in Germany is the Metering Point Operating Act (German: Messstellenbetriebsgesetz, abbreviated as MsbG). It sets technical specifications for smart meter systems and regulates the equipment of metering points. As can be seen, 3 different cases are classified ….

## Slide 12: Smart Grids and Smart Meter enable Smart Markets – Happy Power Hour
reduce power
original load profile
optimized load profile
price-signal
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
€
increase power
Dynamic Electricity Tariffs for Industry Companies
Reducing of the electricity costs using flexibility
Fully automated marketing and control of flexibility
Consumption side adapts itself by reacting on price signals to the feed-in of the renewable energies

## Slide 13: Conclusions
The German “Energiewende” changes the grid structures fundamentally – both in urban and rural areas!
The Smart Grid solutions:
  Are established
  Avoid expensive grid enhancement in many cases
  … but grid enhancement is necessary, too!
Smart Grids enable Smart Markets
A cost-optimized smart grid solution complemented by inevitable grid enhancement forms the basis for Germany’s “Energiewende”.

## Slide 14: Contact
Wuppertal University
Institute of Power System Engineering
Univ.-Prof. Dr.-Ing. Markus Zdrallek
Rainer Gruenter-Str. 21
42119 Wuppertal, Germany
zdrallek@uni-wuppertel.de
http://www.evt.uni-wuppertal.de
Thank you for your attention!